## Battery Calculations
Instructions: 1) Select the AES product from the AES Product field. 2) Enter the # of hours of standby time required. Remember, AES products are listed for 24 hours. 3) All other fields are locked, the calculator will return the battery size automatically in the field colored green.
AES Product | Standby Current (Amps) |  | QTY |  | Total Standby Current (Amps) | Alarm/Transmit Current (Amps) |  | QTY |  | Total Alarm Current (Amps)
----- | 0 | X | 1 | = | 0 | 0 | X | 1 | = | 0
Total System Standyby Current (Amps) |  |  |  |  | 0 | Total System Alarm Current (Amps) |  |  |  | 0
| ## Hour Standby Time **** |  | Standby Current (Amps) |  | Required Standby Capacity (Amp-Hours) | Required Alarm Time (Hours) |  | Alarm/Transmit Current (Amps) |  | Required Alarm Capacity (Amp-Hours)
| 24 | X | 0 | = | 0 | 0.25 | X | 0 | = | 0
| Required Standby Capacity (Amp-Hours) |  | Required Alarm Capacity (Amp-Hours) |  | Total Capacity (Amp-Hours) | The battery requirements presented are not AES recommendations. For UL listed battery requirements please read the products Installation and Operation Manual.
| 0 | + | 0 | = | 0
| Total Capacity (Amp-Hours) |  | Safety Factor |  | Adjusted Battery Capacity (Amp-Hours)
| 0 | X | 120% | = | 0
Note on B8: AES Corp: Please select your AES Subscriber model.
Note on C13: AES Corp. - Enter a number (in hours) for the total hours required for Standby time. AES products are UL listed for 24 hours.

## Sheet1 (hidden)
Subscriber Type | Standby | transmit
----- | 0 | 0
7007P-M | 0.2 | 1.1
7007P-P-M | 0.36 | 1.45
7170 | 0.37 | 0.9
7707P-44-M | 0.3 | 1.2
7707P-44-ULP-M | 0.4 | 1.55
7707P-88-M | 0.3 | 1.2
7707P-88-ULP-M | 0.4 | 1.55
7058E | 0.15 | 1.5
7788F | 0.15 | 1.2
7788F-ULP | 0.21 | 1.2
7788F-ULP-P | 0.267 | 1.3